Removing the Front Cover

- 1-3   (page 4)

Cable Management

- Cable Entries, Knockout Plates, Cable Fastening, Chassis Connections, 1-4   (page 8)

Fastening the Wallbox

- Preparing the Wall, A:1-2   (page 5)

- Fixing the Wallbox, B:1-4   (page 5)

Mounting DIN Rails (optional)

- Opening the Rectifiers Power Rack, A:1-2   (page 6)

- Mounting DIN Rails (optional) , B:1-3   (page 6)

Preparations

- Tools, Warnings, Block Diagram, Schematics   (page 2-3)

Installing Rectifiers & Opening the Controller

- Mounting and Removing Flatpack2 Rectifiers, A:1-3   (page 7)

- Mounting and Removing Blind Panels, B:1-2   (page 7)

- Opening and Closing the Smartpack2 Master Controller, C:1-2   (page 7)

Electrical Connections

- Connecting AC Main Input, DC Output and I/O Control Signals, A:1-7   (page 9)

- Connecting the Load in 110VDC Power Systems, B:1-5   (page 10)

Check Lists

- Installation Check List

- Commissioning Procedure

Flatpack2 PS System, Bulk Feed DC Output, Wallbox

2 Rectifiers and Smartpack2 Controller System

D = 193.5 mm

W = 452.4 mm

H = 450.3 mm

300 mm

300 mm

1000 mm

Minimum Clearances

100 mm

100 mm

NOTICE:

For technical specifications and functionality description, refer to following documents:

- CTO30210.DS3, Datasheet Flatpack2 Wallbox

- 350002.013, User Guide Flatpack2 Rectifiers

- 350020.013, User Guide Smartpack2 Master Controller

- 350021.013, User Guide Smartpack2 Basic Controller

- 351509.033, Installation Guide I/O Monitor2 CAN Node

- For generic power system functionality, refer to WebPower Online Help and PowerSuite Online Help

CAUTION:

- When using only one rectifier, always mount a blind panel in the unused position (avoids rectifier’s air cooling reduction)

- When using 110VDC Flatpack2 rectifiers (241115.805), always remove the DC load terminal rails — with the M8 bolts and screw terminals — and connect the load to the WDU terminal blocks

WARNING:

- Always remove the rectifiers when transporting the Wallbox. For dismounting instructions, refer to page 7

- When possible, use Flatpack2 HE rectifiers in the Wallbox, as they are more efficient and generate less noise. For suitable rectifier options, refer to the datasheet (CTO30210.DS3)

Warnings	B:

Block Diagram	C:

Tools	A:

Fuse Alarm

LVD Controls

Temp. Sensors

AC Fuses, 
external

(230VAC)

AC Supply

(Single phase)

Flatpack2 HE
rectifiers

CAN Bus

DC Supply

(24V, 48V, 60V
 or 110V)

Ethernet cable

Internet

Smartpack2
Master Controller

Smartpack2
Basic Controller

Alarm Outputs NC-C-NO

Config. Inputs

WebPower

(web-based
user interface)

I/O Monitor2
CAN node

Bulk Feed 
DC Output

Flatpack2 System
Wallbox

Internal

MCBs

Telecom and Industrial 
equipment

LVBD

Battery MCBs

DC Distribution 
Load MCBs

Battery Blocks

Optional 
Equipment

| Torque Recommendations |  |  |
| --- | --- | --- |
|  | Type & Size | Torque (Nm) |
| T1 | Bolts M8 | 12.0 |
| T2 | Screws M5-M6 | 2.0 |
| T5 | PG21 plastic (metal) [cap nut] | 7.5 (10) [5.0] |
| T6 | PG29 plastic (metal) [cap nut] | 7.5 (10) [5.0] |
| T7 | PG36 plastic (metal) [cap nut] | 7.5 (10) [5.0] |

Note: General tolerance: ±10%

Tools

Flat 6mm

AW

PZ2

IW (Insulated)

Preparations	A-D

Flatpack2 System
Wallbox

The figure shows the position of the relay contacts when the PS system is in alarm mode of operation; the relay coils are then de-energized (fail-safe mode). The relay outputs are preprogrammed from factory (Factory Settings).

Input Circuit 1

Input Circuit 2

Input Circuit 3

Input Circuit 4

6

Config. Input

(From external equipment)

3

2

1

4

5

Config. Input

Config. Input

Config. Input

Config. Input

Config. Input

Input Circuit 5

Input Circuit 6

+

–

+

–

–

–

+

–

+

+

+

–

X:***

Programmable Inputs

Max. 1.5 mm2, 
(14AWG) wire section

I/O Monitor2 CAN Node

Relay 1

Common Alarm

Alarm Circuit 1

Alarm Circuit 2

Alarm Circuit 3

Alarm Circuit 4

(To external equipment)

Alarm Circuit 5

Alarm Circuit 6

Alarm Relay Outputs

NO

NC

C

NO

C

NC

C

NO

NC

NO

C

NO

NC

C

NC

X:****

NO

C

NC

Relay 2

Mains Alarm

Relay 3

Fuse Alarm

Load & Battery

Relay 4

High Battery Alarm

Relay 5

Low Battery Alarm

Relay 6

Rectifier Alarm

Max. 1.5 mm2, 
(14AWG) wire section

+

4

3

2

1

5

6

X:**

Configurable Inputs

Temp Sense 1

+

Temp Sense 2

+

Temp Sense 3

Temperature Sensor 1

Temperature Sensor 2

Temperature Sensor 3

Smartpack2 Basic controller

| FUNCTION | SIGNAL | PIN-OUT |
| --- | --- | --- |

(These multipurpose inputs may also be used as digital inputs, e.g. for SPD monitoring)

Cable Lugs for M8 bolts: Diam. 8.5mm, Max. 10.5mm

(Not used in 110VDC systems)

Bulk Feed DC Output

Load Circuit

Wire Section:
35 mm2, (1AWG) screw terminals

(Not used in 110VDC systems)

10 mm2, (6AWG) WDU terminals

(Only used in in 110VDC systems)

—

+

Terminal Rails and 
WDU terminals

| FUNCTION | SIGNAL | TERM. POINT |
| --- | --- | --- |

Max. wire section
L&N: 35 mm2 (1AWG)
 PE: 10 mm2 (6AWG)

PE

AC Mains Input

(Protective Earth)

AC Mains Cable

PE

N

L

F1

F2

32 A

Schematics	D:

A-D	Preparations

2

1

PZ2

(T2)

ccw

Wallbox

(front)

5 mm

5 mm

10 mm

ccw

PZ2

(T2)

S1

S1, S2, S3 = M5 x 20 mm

S2

S3

S2

S1

3

Wallbox’s Front Cover

Removing the Front Cover	1-3

NOTICE:

- Use suitable screws or bolts (not included) to fasten the Wallbox to the wall or support surface (wall plugs, expansion bolts or molly bolts)

CAUTION:

- The wall or support surface must be capable of supporting the equipment

- Check min. clearances for Wallbox access: 
front access, 100 cm; top and bottom access, 30 cm; access at the sides, 10 cm

Diam. 8.5 mm

Diam. 5.5 mm

Keyhole

WARNING:

- Never mount the Wallbox in the vicinity of heaters or above heat sources

Get ready suitable screws or bolts (4x)
 S4, S5, S6, S7

1

388 mm

356 mm

356 mm

388 mm

(2x)

Mark and drill 4 suitable holes in the wall

2

3

PZ2

cw

S4

S5

| Weight |  |  |  |
| --- | --- | --- | --- |
| Parts | Kg | Pcs | Kg |
| FP2 WB ex Rectifiers |  |  | 11.3 |
| FP2 Rectifier | 1.95 | 2 | 3.9 |
| Total weight FP2 WB |  |  | 15.2 |

Note: General tolerance: ±10%

Suitable screw or bolt, S5 (2x)

(2x)

3 mm

388.0

(2x)

388.0

(2x)

356.0

356.0

356.0

452.4

(2x)

450.3

Not in scale

All measurements in mm

57.6

36.8

32.1

(2x)

32.1

(2x)

Wallbox’s outer edge

S4

S5

Wallbox’s Rear Plate

1

Keyhole

(x2)

2

1

2

S4

Suitable screw or bolt, S6 (x2)

3

cw

S7

(2x)

3

(x2)

4

4

PZ2

cw

Fixing the Wallbox	B:1-4

Preparing the Wall	A:1-2

A-B	Fastening the Wallbox

CAUTION:

- Mounted additional equipment is not to touch the rectifiers power rack when in its closed position

1

Wallbox’s Rear Plate

DIN Rail
(for additional equipment)

Mounting Slots

Rectifiers Power Rack (open)

2

Wallbox’s Rear Plate

PZ2

(T2)

3

cw

M6

Smartpack2
Basic Controller

I/O Monitor2
Unit

Smartpack2
Master Controller

M6x50

PZ3 (2x)

(T2)

1

ccw

2

Wallbox’s Rear Plate

Wallbox’s Rear Plate

Rectifiers Power Rack (open)

Mounting DIN Rails (optional)	B:1-3

Opening the Rectifiers Power Rack	A:1-2

Mounting DIN Rails (optional)	A-B

Smartpack2 Master controller (locked)

Handle in locked position

Smartpack2 Master controller (open)

Handle in open position

SD card

1

2

1

Opening the controller

Closing the controller

Pen, or use your fingers

Ethernet socket

Screwdriver 
to release the locking tabs

Blind panel’s upper locking tabs

1

2

1

1

2

Blind Panel

CAUTION:

Mount blind panels in unused rectifier locations.

Removing Blind Panels

Mounting Blind Panels

Flat 6mm

1

Handle 
in unlocked position

Flatpack2 HE rectifier

2

3

Hole to release the handle’s spring mechanism

1

3

Wallbox’s Rear Plate

Handle in locked position

Flatpack2 HE rectifier

CAUTION:

The rectifiers may be warm, but do not hand-carry them by their handles. Open the handles before inserting them into the power shelves (hot-pluggable).

Opening and Closing the Smartpack2 Master Controller	C:1-2

Mounting and Removing Blind Panels	B:1-2

Mounting and Removing Flatpack2 Rectifiers	A:1-3

A-C	Installing Rectifiers & Opening the Controller

Top Cable Entries

PG29 x2 and PG21 x12

AC Mains MCBs

DC Output
Bulk Feed

Chassis Earth 
Connection Screws (PE)

M5 x2

Cable fastening tabs

Bottom Cable Entries

PG29 x2 and PG21 x12

Wallbox’s Rear Plate

3

cw

2

Insert cable

cw

4

AW

(T5)

AW

(T5)

PG 
cable gland

1

Twist off and remove knockout plate

Knockouts (x12x2)

For PG21 cable glands (T5)

Knockouts (x2x2)

For PG29 cable glands (T6)

NOTICE:

Cable entries may be implemented with Thorsman TET grommets, PG cable glands or similar (not included)

PG Cable Gland

Thorsman 
TET grommet

Cable Entries, Knockout Plates, Cable Fastening, Chassis Connections	1-4

Cable Management

5

Insert and connect
“+”&”–“ DC Load cables

(E & F)

E

F

PG 
cable gland

3

Insert and connect 
“L”&”N” AC Mains and “PE” Earth cables

(A & B)

A

B

Wallbox’s Rear Plate

6

Insert and connect
I/O signal cables and Ethernet cable

(C & D)

C

D

Earth Terminal (PE)

Max 10mm2 (6awg) 
(T2)

AC Mains Input

Max 25mm2 (2awg) 
(T2)

AC Mains MCBs
(internal) 32 A

N

L

Chassis Earth 
Connection Screws (PE)

M5 x2

Cable fastening tabs

DIP Switches

I/O Monitor2 Unit

Configurable Inputs

X*** Max 1.5mm2 (14awg)

Input 6

Relay Outputs

X**** Max 1.5mm2 (14awg)

Relay 1

Smartpack2 Basic controller

Temp. Sense Inputs

X** Max 1.5mm2 (14awg)

1+

+

–

Ethernet socket

1

Switch OFF 
external AC Mains MCBs

NOTICE:

For more information about signal and pin-out terminals (X***), refer to Schematics, page 3

2

Switch OFF 
internal AC Mains MCBs

4

Switch OFF 
external Load MCBs

DC Load “–”

M8 bolts (T1) 
Cable Lugs diam. 8.5mm, Max. 10.5mm

DC Load “–”

Screw Terminals 35 mm2,( 1awg) (T1)

DC Load Terminal Rail

(To be removed in 110VDC systems)

7

Fasten all cables

(A & F)

CAUTION:

Before connecting the DC Load cables in step 5, ensure that if the Wallbox is using 110VDC Flatpack2 rectifiers (241115.805), you must always first remove the DC load terminal rails — with the M8 bolts and screw terminals — and connect the load to the WDU terminal blocks, as explained in section B, page 10.

| Current Max. | Ext. Fuse | Ext. Fuse |
| --- | --- | --- |
| AC input (A) 205VAC 185VAC | Type Th/Mag 205VAC 185VAC | Type Hy/Mag 205VAC 185VAC |
| 21.5 24.0 | ← 25A-D → | ← 25A-C2 → |

Doc 2020432,3v0

Recommended External AC Fuses
Flatpack2 Wallbox ~ Systems with 2000W Rectifiers

- Use the values in the 185VAC column, 
if you are unsure or know that the available AC mains voltage may drop below 205VAC

- The recommendations apply for use of 
– Thermal magnetic circuit breaker (Th/Mag), type Siemens 5SX or 5SY series, MG C60H series or similar; and
– Hydraulic magnetic breaker (Hy/Mag), type CBI QF frame or QY frame, Airpax or similar

For installations in USA and Canada only!

– The installation has to comply with the NEC/CEC requirements

– The power system must be equipped with branch circuit protection that complies with NEC/CEC requirements and have a rating at minimum 32A

– For supply connectors, use wire suitable for at least 75ºC (167ºF), type: FEPW, RH, RHW, THHW, YHW, THWN, ZHHW, USE, ZX or similar. Use copper conductors only

UL Approved System Ambient Temperatures

with Specified DC Cables and DC Load Breakers

| System’s Ambient Temp | DC Cables’ Temp Rating | DC Load Breaker |
| --- | --- | --- |
| Max. 50°C | 60°C, Cu wire** | Max. 15A |
| Max. 50°C | 75°C, Cu wire | Max. 20A |

** Default UL approved DC cables

PZ2

IW

Flat

Connecting AC Main Input, DC Output and I/O Control Signals	A:1-7

A-B	Electrical Connections

“–” DC Terminal Rail 3

“–” DC Terminal Rail 4

“+” DC Terminal Rail 1

“+” DC Terminal Rail 2

Terminal rails fastening bolts “B3”&”B4”

WDU terminals 
(for rail fastening)

1

Unscrew internal “+” & “–” DC Output cables (4x) from the terminal rails

2

Unscrew and remove both terminal rails fastening M6 bolts, B1, B2, B3 & B4

4

Connect the internal “+” & “–” DC Output cables (4x) to the WDU terminals

5

Connect the external “+” & “–” DC Load cables to the WDU terminals

Wire Section 10 mm2 (6AWG)

Terminal rails fastening bolts “B1”&”B2”

M6 bolt “B2”

M6 bolt “B4”

3

Unscrew the WDU terminals (2x2) and remove the terminal rails 1, 2, 3 & 4

WDU terminals 
(for rail fastening)

E

F

Internal “+” & “–” 
DC Output cables (4x)

IW

Flat

Flat

Flat

Flat

Connecting the Load in 110VDC Power Systems	B:1-5

Electrical Connections	A-B

This page has intentionally been left empty

PULLOUT

Check Lists Pullout

Pull out the pages with the gray outer band, 
and use them as check lists

Instructions to create the PDF publication with the Pullout Section in the middle, between pages 6 and 7 (12/2):

- Create the PDF file from the Word document

- In Adobe Acrobat:
- Rotate pages 13 through 16, 180 degrees
- Move pages 13 through 16 in between pages 6 and 7
- Save the PDF file

Form 178-gb-v1-C01_354034-103_1v0

commissioning procedure

System Data	Flatpack2 Wallbox PS System

| Supplier’s Order No.: | Flatpack2 Wallbox Power Supply System, type: |  |  | Article No.: |
| --- | --- | --- | --- | --- |
| Site, name: |  |  |  |  |
| Serial No.: |  | Software, version No.: |  | Rectifiers, type & number of: |
| AC Input Voltage, measured: |  | Battery Type, if applicable: | Battery Capacity: | Commissioning carried out by, name: |

Pre-Start Check	Power is OFF!

| check following: | ok |
| --- | --- |
| - Flatpack2 Wallbox system installation is completed; All cabling is securely terminated with correct polarity |  |
| - All external load MCBs/ fuses are switched OFF |  |
| - AC input cable(s) and AC earth wire (PE) are terminated |  |
| - Site specific parameters and settings are known |  |
| - AC supply and all external and internal MCBs/ fuses are switched OFF |  |

Start-up, No-Load & Load Adjustments	Power is ON!

| carry out following: | ok |
| --- | --- |
| - Disconnect all rectifier modules, without removing them (keep original location) |  |
| - Switch ON the system (external and internal AC MCBs/fuses ON) |  |
| - AC input voltage is correct; Measure and verify |  |
| - Insert all Flatpack2 rectifiers in their original locations in the power rack |  |
| - The Smartpack2 Master and all rectifier modules are working, LEDs are ON; Verify |  |
| - Connect a PC to the PS system Use a standard Ethernet cable and access the controller |  |
| - DC output voltage; Measure and adjust |  |
| - Alarm relay test; Verify all alarm relays are working correctly |  |
| - System Setup is in accordance with configuration Enter site spec. info via front keys or PC |  |
| - Connect all external load MCBs/ fuses, and verify no alarms are displayed |  |

Approval

| Responsible of commissioning, sign.: | Date: | Approved by customer, sign.: |
| --- | --- | --- |

I

II

Device
Hazard

Device
Hazard

PULLOUT

www.eltekvalere.com

| Headquarters: Eltek Valere Gråterudv. 8, PB 2340 Strømsø, 3003 Drammen, Norway Phone: +47 32 20 32 00 Fax: +47 32 20 32 10 |  |
| --- | --- |

PULLOUT

This page has intentionally been left empty

Instructions to create the PDF publication with the Pullout Section in the middle, between pages 6 and 7 (12/2):

- Create the PDF file from the Word document

- In Adobe Acrobat:
- Rotate pages 13 through 16, 180 degrees
- Move pages 13 through 16 in between pages 6 and 7
- Save the PDF file

Check Lists Pullout

Pull out the pages with the gray outer band, 
and use them as check lists

PULLOUT